## Readme
enVerid COVID-19 Energy Estimator |  |  |  | For your own copy, select File (top left) --> Make a Copy OR Download to Excel
Developed by: | Marwa Zaatari, Anurag Goel, Sean Joseph
Come back for new versions
For more info: | https://tinyurl.com/energy-estimator-pr
<link for providing feedback>
Version & date | 0.1.3 | 2020-12-02
What we are trying to estimate
Operating, maintenance, first costs, and carbon costs associated with ventilation, filtration, and air cleaning mitigation strategies intended to reduce the propagation of COVID-19 by aerosol transmission.
How to use the estimator
This online version will be kept up-to-date. We can't allow people to make changes to the online version, as otherwise people would overwrite each other's changes
People interested in using the model should download an Excel version from File --> Download or make a G Sheets copy with File --> Make a copy
Or you can download an Excel version with the direct link above
The online model will continue to be updated, so you may want to re-download the file later on, if you continue to use it, to get the latest updates
See the version log at the bottom of this sheet for a brief description of the updates
Inputs and Outputs
Inputs are colored in orange
| Outputs are colored in blue. |  | These are the final results of the model for each case. These values can be overwritten, but note that once overwritten these calculated values can no longer be updated.
Suggestions and improvements
Please provide suggestions for improvements using this link: |  |  |  |  | <link for providing feedback>
Calculation Methodology
Annual Operating Costs - Ventilation
General. 2017 ASHRAE Handbook—Fundamentals calculations are used to calculate cooling and heating energy consumption associated with conditioning outside air. By default, energy consumption is calculated assuming building occupied hours are between 7AM and 7PM, Monday through Saturday. When default occupancy hours are over-written with custom values, the default energy calculations are scaled. This is discussed in more detail in the section below.
Cooling Energy. Sensible and latent cooling energy is computed for each hour of building occupancy.
For each occupied hour:
Where,
4.5 = Total heat conversion factor to BTU/hr
Q_OA = outdoor airflow (CFM)
h_oa = outdoor air enthalpy calculated from TMY3 weather data (BTU/lb)
h_da = discharge air enthalpy setpoint, assumed to be 23 (BTU/lb)
COP is the coefficient of performance
Heating Energy. Sensible heating energy is computed for each hour of building occupancy.
For each occupied hour:
Where,
1.08 = Sensible heat conversion factor to BTU/hr
Q_OA = outdoor airflow (CFM)
t_oa = outdoor air dry bulb temperature per TMY3 weather data (℉)
t_da = discharge dry bulb air temperature setpoint, assumed to be 70 (°F)
Heating efficiency is the heating efficiency (%)
Cooling and Heating Energy per CFM. Using the above equations, the yearly energy use per 1 CFM of outside air was computed for the top metropolitan areas in the US. A summary of these results can be found in Table 1.
Cooling and Heating Energy Rates. Energy rates for each of the top US metro areas are estimated based upon local utility costs. A summary of these results can be found in Table 1.
Annual Operating Costs – Ventilation. Once Energy use per CFM and Energy cost have been determined, Annual operating cost are estimated based upon user inputs using the following formula.
Where,
C_AO = Annual Operating Cost of Ventilation ($/year)
CE_CFM = Cooling Energy per CFM (kWh/CFM/year)
ER_C = Cooling Energy Rate ($/kWh)
HE_CFM = Heating Energy per CFM (kWh/CFM/year)
ER_H = Heating Energy Rate ($/kWh)
Annual Operating Costs – Filtration
General. Filter Annual Operating expenditure is estimated using the methodology utilized in "HVAC filtration and the Wells-Riley approach to assessing risks of infectious airborne diseases" in the “Cost of HVAC Filtration” section starting on page 30 (Available here: https://www.nafahq.org/wp-content/uploads/WellsRileyReport.pdf). The filter Annual Operating expenditure calculation includes the fan energy component, the filter material cost component, and the labor component of the filter costs.
Carbon Emissions
Carbon emissions were determined from total yearly energy used to kg CO2 using EPA conversion factors found here: https://www.epa.gov/energy/greenhouse-gases-equivalencies-calculator-calculations-and-references
Understanding CADR
Clean air delivery rate is a combination of filter performance and also how much air passes through that filter (e.g., a device with a great filter but no air passing through is not effective)
CADR is determined for different particle sizes; use the smoke or dust rating
A more elaborate calculator for HEPA filters can be found here:
https://docs.google.com/spreadsheets/d/1NEhk1IEdbEi_b3wa6gI_zNs8uBJjlSS-86d4b7bW098/edit#gid=1882881703
If you know the airflow through the device, use Table 2 to get the efficiency, then multiply efficiency by airflow to get CADR
For UVGI devices, you can use a proxy CADR by multiplying the airflow through the UV lights times the reported efficiency. Be sure to consider residence time, the output loss if the UV lights are placed after the cooling coil (cold environment), and depreciation.
Version log
0.1.1
0.1.2 | Corrected table 1 syntax error upon download, replaced readme screenshots with text, corrected readme heating and cooling energy formulas, updated filter pressure drop to IP units.
0.1.3 | Added Raleigh, NC. Added San Jose, CA. Updated heating energy setpoint from 70 degrees F to 55 degrees F. added 24/7 weather data
Planned Improvements as time allows
Include details on default VRP and IAQP calculations
add additional US cities upon request
About enVerid:
enVerid helps buildings achieve ESG (Environmental, Social, and Governance), healthy building, and cost saving goals by improving indoor air quality while saving money and reducing energy consumption and carbon emissions. For new HVAC systems, enVerid’s award-winning HVAC Load Reduction® (HLR) Modules enable immediate capital cost savings. HLR Modules also deliver up to 30% energy savings and superior indoor air quality in new and existing buildings. enVerid’s air filtration products remove particulate and microorganism contamination from indoor air without the significant cost of upgrading mechanical systems and increasing mechanical ventilation rates. enVerid’s products are deployed in commercial, academic and government buildings globally. enVerid’s HLR Modules are ASHRAE Standard 62.1, LEED, and WELL compliant and eligible for utility rebates. For more information please visit https://enverid.com.

## Calculation
enVerid COVID-19 Energy Estimator - Calculations
This is a general spreadsheet applicable to any situation, under the assumptions of this model - See notes specific to this case (if applicable) at the very bottom
Inputs as highlighted in orange - change these for your situation
Specialized inputs or calculated outputs
Results are in blue -- these are the numbers of interest for most people
Parameter | Input/Output | units | Source / Comments
General Inputs
Representative city | Dallas, TX |  | Requests for additional cities can be submitted here.
Space type | Bars, cocktail lounges |  | Primary space type
Floor area | 5500 | ft2
Average ceiling height | 9 | ft
Occupancy | 28 | occupants
Total supply airflow | 5000 | CFM | If you don't know the airflow, assume 1 cfm/ft2. This value must be greater than or equal to outside air value.
System ventilation efficiency | 0.75 |  | Building system ventilation efficiency. Applies to most systems with multiple ventilation zones. Set to 1.0 for single zone buildings. Utilize ASHRAE 62.1 to calculate system ventilation efficiency
OA calculation method | VRP |  | Input building outside air ventilation strategy VRP = Ventilation Rate Procedure, prescriptive approach per ASHRAE Standard 62.1 VRP + 30% = 30% more than the prescriptive approach 100% OA = all the total supply air is outside air IAQP = Indoor Air Quality Procedure, performance-based procesure per ASHRAE Standard 62.1 Other = Manual entry
Outside airflow | 1600 | CFM | Calculated based upon building ventilation strategy and general inputs. Note that this value can be overwritten by the user.
Outside air ACH | 1.9394 | /h | (ACH = Air changes per hour)
Outside air ventilation Energy & Operating Costs Inputs
Outside air ventilation cooling source | Electricity |  | At this time this calculator only supports electric cooling. Chilled water cooling is planned for a future revision.
Outside air ventilation heating source | Gas |  | At this time this calculator only supports electric, natural gas, and steam heating.
Hours per day of building operation | 12 | hours/day | These inputs for COP, heating efficiency, and weekly building operations hours are used to linearly estimate the energy use per cfm for your building. Estimates are based on a COP of 3, an Efficiency of 1.0, and 72 weekly building operational hours. For 24/7 Buildings, a secondary weather data set is utilized.
Days per week of building operation | 6 | days/week
Hours per week of operations | 72 | hours/week
COP | 3
Heating Efficiency | 1
Electricity rate | 0.13458 | $/kWh (blended) | Estimate based upon local utility costs
Heating energy rate | 0.76466 | $/therm | Estimate based upon local utility costs
Energy Recovery Inputs (optional)
Is energy recovery being utilized in this building? | No
Summer energy recovery effectiveness | 0 |  | Enter as a fraction. 1.0=100%. Note that this value should take into account the percent of OA utilizing the energy recovery wheel
Winter energy recovery effectiveness | 0 |  | Enter as a fraction. 1.0=100%. Note that this value should take into account the percent of OA utilizing the energy recovery wheel
Indoor Air Filtration Operating Costs & First Costs Inputs
Is filtration being utilized to clean recirculated air? | Yes
Indoor Air Filtration MERV | MERV 16 |  | Minimum Efficiency Reported Value
Average pressure drop across the filter | 0.63093 | in. w.g. | Pressure Drop across the filter values can be found in Table 3
Fan Efficiency | 0.85
Motor Efficiency | 0.85
Maximum allowable filter airspeed | 500 | fpm | Maximum allowable filter airspeed in feet per min
Estimated filter lifespan | 12 | months
Labor cost of replacing a filter | 5 | $/filter | Estimated labor cost for replacing a single filter
Filtration ACH | 3.9152 | /h
Air Cleaner Operating Cost & First Cost Inputs
Are air cleaners being utlized to clean additional recirculated air? | No
Quantity of air cleaners | 5.5
Air cleaner supply air per air cleaner | 200 | CFM
CADR per air cleaner | 200 | CFM | See readme, row 89
Additional ACH | 1.3333 | /h
First Cost per air cleaner | 2200 | $ | First cost includes hardware plus installation cost if applicable (does not include material costs i.e. filters, lamps, etc.)
Air Cleaner Power | 0.06 | kW/unit
Estimated lifespan before maintenance | 12 | months | Maintenance is scheduled maintenance to replace consumables such as filters, UV lamps, etc.
Labor cost of maintenance | 40 | $/unit | Maintenance is scheduled maintenance to replace consumables such as filters, UV lamps, etc.
Material cost of maintenance | 150 | $/unit | Maintenance is scheduled maintenance to replace consumables such as filters, UV lamps, etc.
Outside air ventilation Energy Consumption & Cost
Cooling Outside Air Ventilation Energy | 18390.4 | kWh/year
Cooling Outside Air Ventilation Energy Cost | 2474.9389 | $/year
Heating Outside Air Ventilation Energy | 213.275 | therm/year | Note that units update automatically based upon ventilation heating source
Heating Outside Air Ventilation Energy Cost | 163.0824 | $/year
Indoor Air Filtration Energy Consumption & Cost
Indoor air filtration fan energy load | 0.34868 | kW | see readme
Annual filtration fan energy | 175.6875 | $/year | Fan energy cost per year = fan energy * operational hours per year * blended electrical energy rate
Material cost of filter replacement | 875 | $/year | Filter Material cost table can be found in Table 3
Labor cost of filter replacement | 35 | $/year | filter labor costs = cost to replace each filter * quantity of filters * replacements per year per filter
Annual filter fan energy and filter replacement costs | 1085.6875 | $/year | operational cost of filters (includes material costs, maintenance costs, and fan energy costs)
Air cleaner Operating Cost & First Cost Outputs
Air Cleaner Annual Energy Consumption | 0 | kWh/year
Air Cleaner Annual Energy Cost | 0 | $/year
Air Cleaner Filter Material Cost | 0 | $/year
Air Cleaner Maintenance Labor Cost | 0 | $/year | Maintenance is scheduled maintenance to replace consumables such as filters, UV lamps, etc.
Air Cleaner Total Annual Cost | 0 | $/year | = Energy cost + material cost + maintenance
Air Cleaner First Cost | 0 | $
Effective Air Changes per Hour (ACH)
Outside air ACH | 1.9394 | /h
Filtration ACH | 3.9152 | /h
Additional ACH | 0 | /h
Effective ACH | 5.8545 | /h | ACH for outside air, filtration, and additional air cleaning
Annual Cost Summary
Annual outside air ventilation energy cost | 2638.0213 | $/year | OpEx
Annual indoor air filter fan energy and filter replacement costs | 1085.6875 | $/year | OpEx + Material Costs + Maintenance
Annual air cleaner energy consumption and maintenance costs | 0 | $/year | OpEx + Material Costs + Maintenance (Does not include first cost of air cleaner)
Total annual costs | 3723.7088 | $/year
Annual Carbon Emissions
Carbon emissions - outside air ventilation energy | 14.1324 | metric tons of CO2/year | see readme
Carbon emissions - filtration fan energy | 0.92297 | metric tons of CO2/year | see readme
Carbon emissions - Air cleaner energy | 0 | metric tons of CO2/year | see readme
Total Carbon Emissions | 15.0553 | metric tons of CO2/year

## Scenario Comparison
enVerid COVID-19 Energy Estimator - Scenario Comparison
This spreadsheet summarizes the ACH and cost for different ventilation and filtration scenarios
Do not change the results in this tab. Any change should be made to the Calculation Tab
| City | Dallas, TX
| Space Type | Bars, cocktail lounges
| Floor Area | 5500
| Occupancy | 28
Notes:
Rows and columns in green show the scenario chosen on the Calculation tab
The other scenarios are calculated to show various scenarios based on the other inputs from the Calculation tab
All other inputs not listed here are common across all scenarios
| Effective ACH | MERV 7 | MERV 11 | MERV 13 | MERV 16
| 100% OA | 6.6667 | 6.6667 | 6.6667 | 6.6667
| VRP+30% | 3.4863 | 5.0765 | 5.9284 | 6.3827
| VRP | 3.3587 | 5.0127 | 5.8987 | 6.3713
| IAQP | 3.12 | 4.8933 | 5.8433 | 6.35
| VRP | 3.3587 | 5.0127 | 5.8987 | 5.8545
| Total Annual Cost | MERV 7 | MERV 11 | MERV 13 | MERV 16
| 100% OA | 9068.1983 | 9068.1983 | 9068.1983 | 9068.1983
| VRP+30% | 1874.3617 | 1920.6237 | 2045.2499 | 2885.2967
| VRP | 1571.2624 | 1619.3807 | 1744.1925 | 2585.0437
| IAQP | 1040.2948 | 1091.8853 | 1229.0443 | 2153.4002
| VRP | 1571.2624 | 1619.3807 | 1744.1925 | 3723.7088
| Outside Air Ventilation - Energy Cost | MERV 7 | MERV 11 | MERV 13 | MERV 16
| 100% OA | 9068.1983 | 9068.1983 | 9068.1983 | 9068.1983
| VRP+30% | 1343.1925 | 1343.1925 | 1343.1925 | 1343.1925
| VRP | 1033.225 | 1033.225 | 1033.225 | 1033.225
| IAQP | 453.4099 | 453.4099 | 453.4099 | 453.4099
| VRP | 1033.225 | 1033.225 | 1033.225 | 2638.0213
| Indoor Air Filtration - Energy Cost + Maintenance Cost | MERV 7 | MERV 11 | MERV 13 | MERV 16
| 100% OA | 0 | 0 | 0 | 0
| VRP+30% | 531.1692 | 577.4312 | 702.0574 | 1542.1042
| VRP | 538.0374 | 586.1556 | 710.9675 | 1551.8187
| IAQP | 586.8848 | 638.4753 | 775.6344 | 1699.9903
| VRP | 538.0374 | 586.1556 | 710.9675 | 1085.6875
| Air Cleaner - Energy Cost + Maintenance Cost | 0
| Parameter | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output | Input/Output
General Inputs
| Representative city | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX | Dallas, TX
| Space type | Bars, cocktail lounges | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space | Office space
| Floor area | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| Average ceiling height | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Occupancy | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
| Total supply airflow | 5000 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500 | 5500
| System ventilation efficiency | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
| OA calculation method | VRP | 100% OA | 100% OA | 100% OA | 100% OA | VRP+30% | VRP+30% | VRP+30% | VRP+30% | VRP | VRP | VRP | VRP | IAQP | IAQP | IAQP | IAQP | VRP | VRP | VRP
| Outside airflow | 1600 | 5500 | 5500 | 5500 | 5500 | 814.6667 | 814.6667 | 814.6667 | 814.6667 | 626.6667 | 626.6667 | 626.6667 | 626.6667 | 275 | 275 | 275 | 275 | 626.6667 | 626.6667 | 626.6667
| Outside air ACH | 1.9394 | 6.6667 | 6.6667 | 6.6667 | 6.6667 | 0.98747 | 0.98747 | 0.98747 | 0.98747 | 0.7596 | 0.7596 | 0.7596 | 0.7596 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.7596 | 0.7596 | 0.7596
Outside air ventilation Energy & Operating Costs Inputs
| Outside air ventilation cooling source | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity
| Outside air ventilation heating source | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas | Gas
| Hours per day of building operation | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Days per week of building operation | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Hours per week of operations | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
| COP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Heating Efficiency | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Electricity rate | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458 | 0.13458
| Heating energy rate | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466 | 0.76466
Energy Recovery Inputs (optional)
| Is energy recovery being utilized in this building? | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No
| Summer energy recovery effectiveness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Winter energy recovery effectiveness | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Indoor Air Filtration Operating Costs & First Costs Inputs
| Is filtration being utilized to clean recirculated air? | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Indoor Air Filtration MERV | MERV 16 | MERV 7 | MERV 11 | MERV 13 | MERV 16 | MERV 7 | MERV 11 | MERV 13 | MERV 16 | MERV 7 | MERV 11 | MERV 13 | MERV 16 | MERV 7 | MERV 11 | MERV 13 | MERV 16 | MERV 7 | MERV 11 | MERV 13
| Average pressure drop across the filter | 0.63093 | 0.44607 | 0.56663 | 0.57869 | 0.63093 | 0.44607 | 0.56663 | 0.57869 | 0.63093 | 0.44607 | 0.56663 | 0.57869 | 0.63093 | 0.44607 | 0.56663 | 0.57869 | 0.63093 | 0.44607 | 0.56663 | 0.57869
| Fan Efficiency | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
| Motor Efficiency | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
| Maximum allowable filter airspeed | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
| Estimated filter lifespan | 12 | 3 | 4 | 4 | 12 | 3 | 4 | 4 | 12 | 3 | 4 | 4 | 12 | 3 | 4 | 4 | 12 | 3 | 4 | 4
| Labor cost of replacing a filter | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| Filtration ACH | 3.9152 | 0 | 0 | 0 | 0 | 2.4988 | 4.089 | 4.9409 | 5.3952 | 2.5991 | 4.2531 | 5.1392 | 5.6117 | 2.7867 | 4.56 | 5.51 | 6.0167 | 2.5991 | 4.2531 | 5.1392
0
| Air Cleaner Operating Cost & First Cost Inputs | 0
| Are air cleaners being utlized to clean additional recirculated air? | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No | No
| Quantity of air cleaners | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
| Air cleaner supply air per air cleaner | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| CADR per air cleaner | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Additional ACH | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333 | 1.3333
| First Cost per air cleaner | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200 | 2200
| Air Cleaner Power | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
| Estimated lifespan before maintenance | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Labor cost of maintenance | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Material cost of maintenance | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
0
| Outside air ventilation Energy Consumption & Cost | 0
| Cooling Outside Air Ventilation Energy | 18390.4 | 63217 | 63217 | 63217 | 63217 | 9363.7787 | 9363.7787 | 9363.7787 | 9363.7787 | 7202.9067 | 7202.9067 | 7202.9067 | 7202.9067 | 3160.85 | 3160.85 | 3160.85 | 3160.85 | 7202.9067 | 7202.9067 | 7202.9067
| Cooling Outside Air Ventilation Energy Cost | 2474.9389 | 8507.6026 | 8507.6026 | 8507.6026 | 8507.6026 | 1260.1564 | 1260.1564 | 1260.1564 | 1260.1564 | 969.3511 | 969.3511 | 969.3511 | 969.3511 | 425.3801 | 425.3801 | 425.3801 | 425.3801 | 969.3511 | 969.3511 | 969.3511
| Heating Outside Air Ventilation Energy | 213.275 | 733.1329 | 733.1329 | 733.1329 | 733.1329 | 108.5925 | 108.5925 | 108.5925 | 108.5925 | 83.5327 | 83.5327 | 83.5327 | 83.5327 | 36.6566 | 36.6566 | 36.6566 | 36.6566 | 83.5327 | 83.5327 | 83.5327
| Heating Outside Air Ventilation Energy Cost | 163.0824 | 560.5957 | 560.5957 | 560.5957 | 560.5957 | 83.0361 | 83.0361 | 83.0361 | 83.0361 | 63.8739 | 63.8739 | 63.8739 | 63.8739 | 28.0298 | 28.0298 | 28.0298 | 28.0298 | 63.8739 | 63.8739 | 63.8739
0
| Indoor Air Filtration Energy Consumption & Cost | 0
| Indoor air filtration fan energy load | 0.34868 | 0 | 0 | 0 | 0 | 0.33972 | 0.43153 | 0.44071 | 0.4805 | 0.35335 | 0.44885 | 0.4584 | 0.49978 | 0.37885 | 0.48124 | 0.49148 | 0.53584 | 0.35335 | 0.44885 | 0.4584
| Annual filtration fan energy | 175.6875 | 0 | 0 | 0 | 0 | 171.1692 | 217.4312 | 222.0574 | 242.1042 | 178.0374 | 226.1556 | 230.9675 | 251.8187 | 190.8848 | 242.4753 | 247.6344 | 269.9903 | 178.0374 | 226.1556 | 230.9675
| Material cost of filter replacement | 875 | 0 | 0 | 0 | 0 | 160 | 210 | 330 | 1250 | 160 | 210 | 330 | 1250 | 176 | 231 | 363 | 1375 | 160 | 210 | 330
| Labor cost of filter replacement | 35 | 0 | 0 | 0 | 0 | 200 | 150 | 150 | 50 | 200 | 150 | 150 | 50 | 220 | 165 | 165 | 55 | 200 | 150 | 150
| Annual filter fan energy and filter replacement costs | 1085.6875 | 0 | 0 | 0 | 0 | 531.1692 | 577.4312 | 702.0574 | 1542.1042 | 538.0374 | 586.1556 | 710.9675 | 1551.8187 | 586.8848 | 638.4753 | 775.6344 | 1699.9903 | 538.0374 | 586.1556 | 710.9675
0
| Air cleaner Operating Cost & First Cost Outputs | 0
| Air Cleaner Annual Energy Consumption | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Air Cleaner Annual Energy Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Air Cleaner Filter Material Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Air Cleaner Maintenance Labor Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Air Cleaner Total Annual Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Air Cleaner First Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
| Effective Air Changes per Hour (ACH) | 0
| Outside air ACH | 1.9394 | 6.6667 | 6.6667 | 6.6667 | 6.6667 | 0.98747 | 0.98747 | 0.98747 | 0.98747 | 0.7596 | 0.7596 | 0.7596 | 0.7596 | 0.33333 | 0.33333 | 0.33333 | 0.33333 | 0.7596 | 0.7596 | 0.7596
| Filtration ACH | 3.9152 | 0 | 0 | 0 | 0 | 2.4988 | 4.089 | 4.9409 | 5.3952 | 2.5991 | 4.2531 | 5.1392 | 5.6117 | 2.7867 | 4.56 | 5.51 | 6.0167 | 2.5991 | 4.2531 | 5.1392
| Additional ACH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Effective ACH | 5.8545 | 6.6667 | 6.6667 | 6.6667 | 6.6667 | 3.4863 | 5.0765 | 5.9284 | 6.3827 | 3.3587 | 5.0127 | 5.8987 | 6.3713 | 3.12 | 4.8933 | 5.8433 | 6.35 | 3.3587 | 5.0127 | 5.8987
0
| Annual Cost Summary | 0
| Annual outside air ventilation energy cost | 2638.0213 | 9068.1983 | 9068.1983 | 9068.1983 | 9068.1983 | 1343.1925 | 1343.1925 | 1343.1925 | 1343.1925 | 1033.225 | 1033.225 | 1033.225 | 1033.225 | 453.4099 | 453.4099 | 453.4099 | 453.4099 | 1033.225 | 1033.225 | 1033.225
| Annual indoor air filter fan energy and filter replacement costs | 1085.6875 | 0 | 0 | 0 | 0 | 531.1692 | 577.4312 | 702.0574 | 1542.1042 | 538.0374 | 586.1556 | 710.9675 | 1551.8187 | 586.8848 | 638.4753 | 775.6344 | 1699.9903 | 538.0374 | 586.1556 | 710.9675
| Annual air cleaner energy consumption and maintenance costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total annual costs | 3723.7088 | 9068.1983 | 9068.1983 | 9068.1983 | 9068.1983 | 1874.3617 | 1920.6237 | 2045.2499 | 2885.2967 | 1571.2624 | 1619.3807 | 1744.1925 | 2585.0437 | 1040.2948 | 1091.8853 | 1229.0443 | 2153.4002 | 1571.2624 | 1619.3807 | 1744.1925
0
| Annual Carbon Emissions | 0
| Carbon emissions - outside air ventilation energy | 14.1324 | 48.58 | 48.58 | 48.58 | 48.58 | 7.1957 | 7.1957 | 7.1957 | 7.1957 | 5.5352 | 5.5352 | 5.5352 | 5.5352 | 2.429 | 2.429 | 2.429 | 2.429 | 5.5352 | 5.5352 | 5.5352
| Carbon emissions - filtration fan energy | 0.92297 | 0 | 0 | 0 | 0 | 0.89923 | 1.1423 | 1.1666 | 1.2719 | 0.93531 | 1.1881 | 1.2134 | 1.3229 | 1.0028 | 1.2738 | 1.3009 | 1.4184 | 0.93531 | 1.1881 | 1.2134
| Carbon emissions - Air cleaner energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Carbon Emissions | 15.0553 | 48.58 | 48.58 | 48.58 | 48.58 | 8.095 | 8.338 | 8.3623 | 8.4676 | 6.4705 | 6.7233 | 6.7486 | 6.8581 | 3.4318 | 3.7028 | 3.7299 | 3.8474 | 6.4705 | 6.7233 | 6.7486

## Table 1 - Operational Info
Table 1: Location Based parameters | The following lookup table contains location based parameters related to cooling and heating energy consumption and rates. This data was calculated using TMY3 weather data for major US cities. If your city is not listed here, pick a nearby city in the same climate zone. You can also request additional cities be added to the tool via our support resources.
12/6 data
IECC climate zone | Cities | State | Cooling energy (kWh/cfm) | Estimated Blended Electricity Rate ($/kWh) | Cooling rate ($/cfm) | Heating energy (therms/cfm) | Heating energy (kWh/cfm) | Heating energy (mmBTU/cfm) | Primary Heating Type | Gas Rate ($/therm) | Steam Rate ($/Mlb) | Heating Rate ($/cfm) | Total Spendings ($/CFM)
3a | Atlanta, GA | Georgia | 8.84 | 0.11686 | 1.0331 | 0.13978 | 4.099 | 0.013978 | Gas | 0.95633 | no data | 0.13367 | 1.1667
4a | Baltimore, MD | Maryland | 6.684 | 0.1454 | 0.97184 | 0.24497 | 7.184 | 0.024497 | Gas | 1.0619 | no data | 0.26014 | 1.232
5a | Boston, MA | Massachusetts | 4.273 | 0.20385 | 0.87106 | 0.34216 | 10.034 | 0.034216 | Gas | 1.2905 | no data | 0.44155 | 1.3126
5a | Chicago, IL | Illinois | 5.127 | 0.11371 | 0.58299 | 0.40958 | 12.011 | 0.040958 | Gas | 0.83846 | no data | 0.34341 | 0.9264
3a | Dallas, TX | Texas | 11.494 | 0.13458 | 1.5468 | 0.1333 | 3.909 | 0.01333 | Gas | 0.76466 | no data | 0.10193 | 1.6488
5a | Detroit, MI | Michigan | 4.662 | 0.12377 | 0.57704 | 0.44146 | 12.946 | 0.044146 | Gas | 0.72571 | no data | 0.32037 | 0.89741
2a | Houston, TX | Texas | 14.43 | 0.12996 | 1.8753 | 0.051184 | 1.501 | 0.0051184 | Gas | 0.76466 | no data | 0.039138 | 1.9145
3c | Los Angeles, CA | California | 5.596 | 0.18577 | 1.0396 | 0.0092752 | 0.272 | 0.00092752 | Gas | 1.0742 | no data | 0.0099635 | 1.0495
1a | Miami, FL | Florida | 19.384 | 0.10781 | 2.0898 | 0.0018073 | 0.053 | 0.00018073 | Gas | 1.187 | no data | 0.0021452 | 2.0919
6a | Minneapolis, MN | Minnesota | 3.928 | 0.12965 | 0.50928 | 0.60848 | 17.844 | 0.060848 | Gas | 0.74313 | no data | 0.45218 | 0.96146
4a | New York, NY | New York | 6.066 | 0.2367 | 1.4358 | 0.28017 | 8.216 | 0.028017 | Gas | 0.97581 | 30 | 0.27339 | 1.7092
4a | Philadelphia, PA | Pennsylvania | 6.335 | 0.12709 | 0.80509 | 0.27645 | 8.107 | 0.027645 | Gas | 1.0219 | no data | 0.28251 | 1.0876
2b | Phoenix, AZ | Arizona | 10.288 | 0.13638 | 1.403 | 0.027894 | 0.818 | 0.0027894 | Gas | 0.87331 | no data | 0.02436 | 1.4274
3a | Raleigh, NC | North Carolina | 8.961 | 0.0931 | 0.83427 | 0.16804 | 4.928 | 0.016804 | Gas | 0.84474 | no data | 0.14195 | 0.97622
3c | Riverside, CA | California | 6.871 | 0.1705 | 1.1715 | 0.028746 | 0.843 | 0.0028746 | Gas | 1.0742 | no data | 0.03088 | 1.2024
3c | San Diego, CA | California | 6.443 | 0.25462 | 1.6405 | 0.0065813 | 0.193 | 0.00065813 | Gas | 1.0742 | no data | 0.0070697 | 1.6476
3c | San Jose, CA | California | 3.819 | 0.2292 | 0.87531 | 0.047467 | 1.392 | 0.0047467 | Gas | 1.07 | no data | 0.05079 | 0.9261
4a | St. Louis, MO | Missouri | 6.794 | 0.10148 | 0.68946 | 0.29919 | 8.774 | 0.029919 | Gas | 0.97786 | no data | 0.29257 | 0.98203
2a | Tampa, FL | Florida | 16.926 | 0.11348 | 1.9208 | 0.01705 | 0.5 | 0.001705 | Gas | 1.187 | no data | 0.020238 | 1.9411
4a | Washington DC | District of Columbia | 6.716 | 0.1445 | 0.97046 | 0.25343 | 7.432 | 0.025343 | Gas | 1.1808 | no data | 0.29925 | 1.2697
24/7 data
IECC climate zone | Cities | State | Cooling energy (kWh/cfm) | Estimated Blended Electricity Rate ($/kWh) | Cooling rate ($/cfm) | Heating energy (therms/cfm) | Heating energy (kWh/cfm) | Heating energy (mmBTU/cfm) | Primary Heating Type | Gas Rate ($/therm) | Steam Rate ($/Mlb) | Heating Rate ($/cfm) | Total Spendings ($/CFM)
3a | Atlanta, GA | Georgia | 18.092 | 0.11686 | 2.1143 | 0.38366 | 11.251 | 0.038366 | Gas | 0.95633 | no data | 0.36691 | 2.4812
4a | Baltimore, MD | Maryland | 13.4 | 0.1454 | 1.9483 | 0.69823 | 20.476 | 0.069823 | Gas | 1.0619 | no data | 0.74146 | 2.6898
5a | Boston, MA | Massachusetts | 8.492 | 0.20385 | 1.7311 | 0.90536 | 26.55 | 0.090536 | Gas | 1.2905 | no data | 1.1683 | 2.8995
5a | Chicago, IL | Illinois | 9.972 | 0.11371 | 1.1339 | 1.0841 | 31.792 | 0.10841 | Gas | 0.83846 | no data | 0.90898 | 2.0429
3a | Dallas, TX | Texas | 23.656 | 0.13458 | 3.1836 | 0.32163 | 9.432 | 0.032163 | Gas | 0.76466 | no data | 0.24594 | 3.4295
5a | Detroit, MI | Michigan | 8.939 | 0.12377 | 1.1064 | 1.1261 | 33.024 | 0.11261 | Gas | 0.72571 | no data | 0.81723 | 1.9237
2a | Houston, TX | Texas | 30.61 | 0.12996 | 3.9781 | 0.17793 | 5.218 | 0.017793 | Gas | 0.76466 | no data | 0.13606 | 4.1141
3c | Los Angeles, CA | California | 10.518 | 0.18577 | 1.954 | 0.042625 | 1.25 | 0.0042625 | Gas | 1.0742 | no data | 0.045788 | 1.9997
1a | Miami, FL | Florida | 42.743 | 0.10781 | 4.6081 | 0.0069905 | 0.205 | 0.00069905 | Gas | 1.187 | no data | 0.0082975 | 4.6164
6a | Minneapolis, MN | Minnesota | 7.407 | 0.12965 | 0.96035 | 1.5337 | 44.977 | 0.15337 | Gas | 0.74313 | no data | 1.1398 | 2.1001
4a | New York, NY | New York | 12.513 | 0.2367 | 2.9618 | 0.72691 | 21.317 | 0.072691 | Gas | 0.97581 | 30 | 0.70933 | 3.6712
4a | Philadelphia, PA | Pennsylvania | 12.775 | 0.12709 | 1.6235 | 0.74386 | 21.814 | 0.074386 | Gas | 1.0219 | no data | 0.76017 | 2.3837
2b | Phoenix, AZ | Arizona | 20.993 | 0.13638 | 2.8629 | 0.092718 | 2.719 | 0.0092718 | Gas | 0.87331 | no data | 0.080971 | 2.9439
3a | Raleigh, NC | North Carolina | 18.137 | 0.0931 | 1.6886 | 0.5069 | 14.865 | 0.05069 | Gas | 0.84474 | no data | 0.4282 | 2.1168
3c | Riverside, CA | California | 10.98 | 0.1705 | 1.872 | 0.16085 | 4.717 | 0.016085 | Gas | 1.0742 | no data | 0.17279 | 2.0448
3c | San Diego, CA | California | 12.777 | 0.25462 | 3.2533 | 0.03352 | 0.983 | 0.003352 | Gas | 1.0742 | no data | 0.036008 | 3.2893
3c | San Jose, CA | California | 5.844 | 0.2292 | 1.3394 | 0.19816 | 5.811 | 0.019816 | Gas | 1.07 | no data | 0.21203 | 1.5515
4a | St. Louis, MO | Missouri | 13.955 | 0.10148 | 1.4162 | 0.78331 | 22.971 | 0.078331 | Gas | 0.97786 | no data | 0.76597 | 2.1821
2a | Tampa, FL | Florida | 36.036 | 0.11348 | 4.0895 | 0.058788 | 1.724 | 0.0058788 | Gas | 1.187 | no data | 0.06978 | 4.1593
4a | Washington DC | District of Columbia | 13.174 | 0.1445 | 1.9036 | 0.76098 | 22.316 | 0.076098 | Gas | 1.1808 | no data | 0.89857 | 2.8022

## Table 2 - Filtration Info
Table 2: Filtration Information
Filter Costs, Pressure Drop, Lifespan and efficiency
| filter | size | cost | initial pressure drop (in.w.c.) | final pressure drop (in.w.c.) | average pressure drop (in.w.c.) | filter lifespan (months) | Filter Efficiency (%)
| MERV 4 | 24x24x2 | 2 | 0.08841 | 0.50233 | 0.29336 | 3 | 11%
| MERV 7 | 24x24x2 | 4 | 0.28934 | 0.59878 | 0.44607 | 3 | 44%
| MERV 11 | 24x24x2 | 7 | 0.32551 | 0.75149 | 0.56663 | 4 | 72%
| MERV 13 | 24x24x2 | 11 | 0.36168 | 0.75149 | 0.57869 | 4 | 87%
| MERV 14 | 24x24x12 | 50 | 0.51037 | 1.0006 | 0.75551 | 12 | 89%
| MERV 15 | 24x24x12 | 90 | 0.28131 | 1.0006 | 0.63897 | 12 | 90%
| MERV 16 | 24x24x12 | 125 | 0.26121 | 1.0006 | 0.63093 | 12 | 95%
| HEPA | 24x24x12 | 150 | 1.0006 | 2.0013 | 1.503 | 12 | 99.9%
Reference: HVAC filtration and the Wells-Riley approach to assessing risks of infectious airborne diseases Table 10
* Pressure drop for MERV 11 and MERV 13 reference: Marwa Zaatari, Atila Novoselac, Jeffrey Siegel. 2014. The relationship between filter pressure drop, indoor air quality, and energy consumption in rooftop HVAC units. Building and Environment Volume 73, March 2014, Pages 151-161
https://www.nafahq.org/understanding-merv-nafa-users-guide-to-ansi-ashrae-52-2/

## Table 3 - ASHRAE 62.1 OA Rates
Table 3 - ASHRAE 2016 62.1 OA rates
Occupancy Category | People Outdoor Air Rate Rp (cfm/person) | Area Outdoor Air Rate Ra (cfm/ft2)
Art classroom | 10 | 0.18
Auditorium seating area | 5 | 0.06
Bank vaults/safe deposit | 5 | 0.06
Banks or bank lobbies | 7.5 | 0.06
Barracks sleeping areas | 5 | 0.06
Bars, cocktail lounges | 7.5 | 0.18
Bedroom/living room | 5 | 0.06
Birthing room | 10 | 0.18
Booking/waiting | 7.5 | 0.06
Bowling alley (seating) | 10 | 0.12
Break rooms (food service) | 5 | 0.06
Breakrooms (office) | 5 | 0.12
Cafeteria/fast-food dining | 7.5 | 0.18
Cell | 5 | 0.12
Class 1 imaging rooms | 5 | 0.12
Classrooms (age 9 plus) | 10 | 0.12
Classrooms (ages 5 to 8) | 10 | 0.12
Coffee stations | 5 | 0.06
Common corridors | — | 0.06
Computer (not printing) | 5 | 0.06
Computer lab | 10 | 0.12
Conference/meeting | 5 | 0.06
Corridors | — | 0.06
Courtrooms | 5 | 0.06
Daycare (through age 4) | 10 | 0.18
Dayroom | 5 | 0.06
Dental operatory | 10 | 0.18
Disco/dance floors | 20 | 0.06
Gambling casinos (no smoking) | 7.5 | 0.18
Game arcades | 7.5 | 0.18
General examination room | 7.5 | 0.12
Guard stations | 5 | 0.06
Gym, sports arena (play area) | 20 | 0.18
Health club/aerobics room | 20 | 0.06
Health club/weight rooms | 20 | 0.06
Lecture classroom | 7.5 | 0.06
Lecture hall (fixed seats) | 7.5 | 0.06
Legislative chambers | 5 | 0.06
Libraries | 5 | 0.12
Lobbies | 5 | 0.06
Lobbies/prefunction | 7.5 | 0.06
Main entry lobbies | 5 | 0.06
Mall common areas | 7.5 | 0.06
Manufacturing where hazardous materials are not used | 10 | 0.18
Media center | 10 | 0.12
Multipurpose assembly | 5 | 0.06
Multiuse assembly | 7.5 | 0.06
Museums (children’s) | 7.5 | 0.12
Museums/galleries | 7.5 | 0.06
Music/theater/dance | 10 | 0.06
Occupiable storage rooms for dry materials | 5 | 0.06
Occupiable storage rooms for liquids or gels | 5 | 0.12
Office space | 5 | 0.06
Other dental treatment areas | 5 | 0.06
Pharmacy (prep. area) | 5 | 0.18
Photo studios | 5 | 0.12
Physical therapy exercise area | 20 | 0.18
Physical therapy individual room | 10 | 0.06
Places of religious worship | 5 | 0.06
Prosthetics and orthotics room | 10 | 0.18
Psychiatric consultation room | 5 | 0.06
Psychiatric examination room | 5 | 0.06
Psychiatric group room | 5 | 0.06
Psychiatric seclusion room | 10 | 0.06
Reception areas | 5 | 0.06
Restaurant dining rooms | 7.5 | 0.18
Sales | 7.5 | 0.12
Shipping/receiving | 10 | 0.12
Sorting, packing, light assembly | 7.5 | 0.12
Spectator areas | 7.5 | 0.06
Speech therapy room | 5 | 0.06
Stages, studios | 10 | 0.06
Supermarket | 7.5 | 0.06
Telephone closets | — | 0
Telephone/data entry | 5 | 0.06
Transportation waiting | 7.5 | 0.06
Urgent care examination room | 7.5 | 0.12
Urgent care observation room | 5 | 0.06
Urgent care treatment room | 7.5 | 0.18
Urgent care triage room | 10 | 0.18